## Slide 1: The path to decarbonization for Applied HVAC Systems
Part 1: Overview
DISCLAIMER: This presentation is intended only for educational purposes and does not replace independent professional judgment and/or legal advice. This presentation is copyrighted and cannot be used without the express permission of Daikin Applied Americas Inc.
Presented by: Jeff Seewald, HVAC Systems Business Development Manager

## Slide 2: Introductions
Jeffrey Seewald, PE, CEM
HVAC Systems Business Development Manager
jeffrey.seewald@daikinapplied.com
Joined Daikin in November 2023
30 years of experience
    HVAC equipment and systems
    Building automation and controls
    Energy efficiency and infrastructure renewal
Focus areas at Daikin include:
    Decarbonization
    Refrigerants
    Electrification and heat pumps
    Energy efficiency
    Indoor air quality

## Slide 3: Disclaimer
This content subject to change without notice and is intended only for educational purposes and does not replace independent professional judgment and/or legal advice. The ultimate responsibility is on the engineer of record to ensure the design complies with all applicable codes and Daikin Applied will not accept responsibility or liability for actions that result from the information shared in this presentation. This content is copyrighted and cannot be used without the express permission of Daikin Applied Americas Inc.
Always consult your state & local codes, which may take precedence over standards which vary in adoption, complete or partial, by state. Also note that a state may adopt a different year of the standard than the latest version.
The local Authority Having Jurisdiction (AHJ) has the final authority in interpreting code requirements.

## Slide 4: Agenda
Decarbonization Drivers
Energy & Electricity
Decarbonization
  Refrigerants
  Electrification
  Efficiency
Refrigerants
Low GWP
LCCP
Electrification
Heat pumps
System design & optimization
Efficiency
Load reduction
Ventilation

## Slide 6: Decarbonization drivers

## Slide 7: Addressing Efficiency Needs

## Slide 8: Addressing Efficiency Needs
Codes, Standards & Regulations
System & Design Changes
Efficiency-Enabling Technologies
Include:
ASHRAE Standards
  62.1 - IAQ
  90.1 - Energy
  228 - Net zero energy
  240 - GHG emissions
DOE requirements
CA Title 24
Local codes

## Slide 9: Addressing Efficiency Needs
Codes, Standards & Regulations
System & Design Changes
Efficiency-Enabling Technologies
Include:
    VFD/inverter compressors
    Permanent magnet motors
    Variable volume ratio compression
    Better and larger heat exchangers
    Integrated ‘free-cooling’

## Slide 10: Addressing Efficiency Needs
Codes, Standards & Regulations
System & Design Changes
Efficiency-Enabling Technologies
Include:
More efficient designs
  Load reduction (lighting, insulation, ventilation)
Building recommissioning or energy audits
Systems that share energy within the building or system
  District systems
  Heat recovery
  Heat pumps

## Slide 11: Regulations and Legislation Summary

## Slide 12: Regulations and Legislation Summary
Federal
State
New administration and changing political landscape
Inflation Reduction Act
  Investment in green infrastructure
AIM Act
  Lower GWP Refrigerants
CHIPs and Science Act
  Invest in MFG for semiconductors and R&D for many items including clean energy
Biden-Harris Federal Building Performance Standards
  Electrify 30% of spaces by 2030

## Slide 13: Regulations and Legislation Summary
Federal
State/Local
Building Performance Standards
NYC, Washington, D.C.; St. Louis, MO; and Washington State
Pre-wiring for Electrification
Washington D.C. and Boston
Net-Zero Designs
~11 states with current or future targets
Optimize building efficiency / minimize energy use
Building to generate as much clean energy as it consumes
Gas Bans
Various cities, some legal challenges

## Slide 14: Energy Code Adoption by State
Status of State Energy Code Adoption: Commercial Buildings
Energy code updated in 2024:
Illinois
Minnesota
New Mexico
Ohio
Virginia
Source: US DOE Building Energy Codes Program (January 2025)

## Slide 15: State/Local Building Performance Standards
© 2025 Daikin Applied
Source: US DOE Building Energy Codes Program (January 2025)

## Slide 16: Gas Bans & Gas Ban Bans
WA
OR
ID
NV
CA
AZ
UT
MT
WY
CO*
NM
TX
ND
SD
NE
KS
MN
WI*
MI
IA
MO
IN
IL
ME
NY
PA
OH
KY
TE
NC*
VA*
WV
SC
GA
AL
MS
LA
AR
FL
NJ
VT
NH
MA
CT
MD
DE
OK
© 2025 Daikin Applied

## Slide 17: Embodied vs Operational
Produce
Build
Use
Deconstruct
Reuse
Time
Embodied
Carbon
Embodied
Carbon
Embodied & Operational
Extract/Mine
Transport to Factory
Manufacture
Transport material to site
Construction
Operate building
Maintenance
Tear down
Transport off-site
Dispose
Reuse or recover
Upcycle
Environmental Product Declarations (EPD’s), ISO 14044, ASTM E2921, EN15978
ASHRAE Standard 228 (operational focus)
Including use of refrigerants

## Slide 18: Energy & Electricity

## Slide 21: Estimated US Energy Consumption

## Slide 23: Decarbonization in HVAC
Electrification
Refrigerants
Efficiency
Decarbonization

## Slide 24: Decarbonization in HVAC
Electrification
  Convert fossil fuel equipment/processes to electric
  Dependent on clean power grid
Electrification
Refrigerants
Efficiency
Decarbonization

## Slide 25: Decarbonization in HVAC
Refrigerants
  Can have much higher global warming potential per pound than CO2
  Direct effect: greenhouse effect of the gas
  Indirect effect: change in efficiency changes power usage over equipment lifecycle
  Life Cycle Climate Performance (LCCP): combines direct and indirect effect into one metric
Electrification
Refrigerants
Efficiency
Decarbonization

## Slide 26: Decarbonization in HVAC
Efficiency
  Greatest impact with ‘dirty’ grid
  Reduced (but not zero) impact as grid converts to renewable
Electrification
Refrigerants
Efficiency
Decarbonization

## Slide 27: Challenge of Decarbonization
44°F
60°F
Heat Pump
Cooling

## Slide 28: Challenge of Decarbonization
130°F
100°F
Heat Pump
Boiler
Heating

## Slide 29: Refrigerants

## Slide 30: Global Warming Potential

## Slide 31: GWP is Not the Full Measure of Emissions
  Majority of climate impact from HVAC is electrical power generation over equipment lifetime
  A lower GWP refrigerant with lower efficiency could actually create more global warming!
Direct Effect from Refrigerant
Indirect Effect from Energy Use
Life Cycle Climate Performance
(LCCP)
Source: Zhang M., et al. 2011. “Life Cycle Climate Performance Model for Residential Heat Pump Systems.” AHRTI Report 09003-01

## Slide 32: Lifetime Emissions
*Comparison is made using the Life Cycle Climate Performance (LCCP) metric, measured in kg-CO2.eq. LCCP analysis was performed using a high efficiency HP (24+ SEER), using performance gains claimed by respective refrigerant manufacturer, for a residential sized (9000 Btu/h cooling capacity), installed in Houston, TX climate zone, with an assumed annual leakage rate of 4% and end of life refrigerant leakage of 15% with a 15 year lifetime. The heating COP and SEER were adjusted based on refrigerant characteristics and performance. The physical system size, trim charge requirements and capacity were kept consistent to ensure a like-to-like comparison.

## Slide 33: Electrification

## Slide 34: Grid Emissions
Evaluate carbon emissions using grid emissions factors
Grid emissions factors vary by state/region
Grid emissions also vary by time of day
    Marginal emissions factors
Source: US EPA eGRID

## Slide 35: Grid Emissions
Evaluate carbon emissions using grid emissions factors
Grid emissions factors vary by state/region
Use Power Profiler
https://www.epa.gov/egrid/power-profiler#
Source: US EPA eGRID

## Slide 36: Grid Emissions
Grid emissions vary considerably based on location
MN: 920
WI: 1402
Source: US EPA eGRID
TX: 738
CA: 437
NY: 975
NJ: 595
OR: 632

## Slide 37: Heat Pumps
© 2025 Daikin Applied

## Slide 38: Types of Heat Pumps
Cold
Air In
Hot
water Out
Cold
Water
In
Hot
Water
Out
Water to Water
Heat Pump
Air to Water
Heat Pump
© 2025 Daikin Applied

## Slide 39: Heat Pumps Continued…
Cold
Air In
Hot
Air Out
Cool Water In
Hot Air Out
Water to Air
Heat Pump
Air to Air
Heat Pump
© 2025 Daikin Applied

## Slide 40: Applying Heat Pumps
© 2025 Daikin Applied

## Slide 41: Air To Water HP Capacity vs Ambient Temperature
Chart: 
| 60 | 45 | 25 | 20 | 15
 | 357.5776 | 292.6814 | 222.2918 | 206.0848 | 189.8778
Heating Capacity
MBH
Outdoor Air Temperature °F
© 2025 Daikin Applied

## Slide 42: Air To Water HP Capacity vs Ambient Temperature
Chart: 
| 60 | 45 | 25 | 20 | 15
 | 357.5776 | 292.6814 | 222.2918 | 206.0848 | 189.8778
Heating Capacity
MBH
Outdoor Air Temperature °F
© 2025 Daikin Applied

## Slide 43: Air To Water HP Capacity vs Ambient Temperature
Chart: 
| 60 | 45 | 25 | 20 | 15
 | 357.5776 | 292.6814 | 222.2918 | 206.0848 | 189.8778
Heating Capacity
MBH
Outdoor Air Temperature °F
© 2025 Daikin Applied

## Slide 44: Supply Temperature vs Ambient Temperature
Chart: 
| -5 | 15 | 35 | 95 | 95
 | 100 | 120 | 140 | 140 | 98.6
Max Supply Water Temp.
°F
Outdoor Air Temperature °F
© 2025 Daikin Applied

## Slide 45: Supply Temperature vs Ambient Temperature
Chart: 
| -5 | 15 | 35 | 95 | 95
 | 100 | 120 | 140 | 140 | 98.6
Max Supply Water Temp.
°F
Outdoor Air Temperature °F
© 2025 Daikin Applied

## Slide 46: Supply Temperature vs Ambient Temperature
Chart: 
| -5 | 15 | 35 | 95 | 95
 | 100 | 120 | 140 | 140 | 98.6
Max Supply Water Temp.
°F
Outdoor Air Temperature °F
© 2025 Daikin Applied

## Slide 47: Selecting Based on Worst Case
Chart: 
| 60 | 45 | 25 | 20 | 15
 | 357.5776 | 292.6814 | 222.2918 | 206.0848 | 189.8778
Outdoor Air Temperature
Heat Load
Heat Pump
Capacity
Lowest Temp.
OVERSIZED
© 2025 Daikin Applied

## Slide 48: Design Conditions
Chart: 
| 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
 | 4 | 2 | 3 | 12 | 10 | 12 | 10 | 10 | 18 | 15 | 25 | 21 | 28 | 37 | 34 | 21 | 30 | 33 | 37 | 39 | 57 | 61 | 90 | 85 | 79 | 129 | 84 | 96 | 134 | 106 | 111 | 109 | 111 | 122 | 105 | 75 | 92 | 102 | 86 | 76 | 75 | 77 | 87 | 79 | 93 | 105 | 83 | 106 | 121 | 91 | 109 | 71 | 88 | 104 | 88 | 140
Outdoor Air Temperature °F
Chart: 
| 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
 | 4 | 2 | 3 | 12 | 10 | 12 | 10 | 10 | 18 | 15 | 25 | 21 | 28 | 37 | 34 | 21 | 30 | 33 | 37 | 39 | 57 | 61 | 90 | 85 | 79 | 129 | 84 | 96 | 134 | 106 | 111 | 109 | 111 | 122 | 105 | 75 | 92 | 102 | 86 | 76 | 75 | 77 | 87 | 79 | 93 | 105 | 83 | 106 | 121 | 91 | 109 | 71 | 88 | 104 | 88 | 140
Number Of Hours
Per Each Temperature
© 2025 Daikin Applied

## Slide 49: Design Conditions
“Don’t let the perfect be the enemy of the good”
Chart: 
| 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
 | 4 | 2 | 3 | 12 | 10 | 12 | 10 | 10 | 18 | 15 | 25 | 21 | 28 | 37 | 34 | 21 | 30 | 33 | 37 | 39 | 57 | 61 | 90 | 85 | 79 | 129 | 84 | 96 | 134 | 106 | 111 | 109 | 111 | 122 | 105 | 75 | 92 | 102 | 86 | 76 | 75 | 77 | 87 | 79 | 93 | 105 | 83 | 106 | 121 | 91 | 109 | 71 | 88 | 104 | 88 | 140
Number Of Hours
Per Each Temperature
Outdoor Air Temperature °F
1%
99%
© 2025 Daikin Applied

## Slide 50: Design Conditions
0.047%
1.675%
Source: ASHRAE Weather Data Viewer, for NY, NY (LGA)
LGA
NY
0.594%
15°F
5°F
20°F

## Slide 51: Design Conditions
Source: ASHRAE Weather Data Viewer, for MSP
MSP
MN
1.26%
2.58%
9.96%
0°F
15°F
-5°F

## Slide 52: Design Conditions
Source: ASHRAE Weather Data Viewer, for CLT
CLT
NC
0.067%
0.305%
15°F
20°F

## Slide 53: Selecting Heat Pumps
Outdoor Air Temperature
Heat Load
Heat Pump
Capacity
-10°F
15°F
Heat Pump
+
Supplemental
0F
30°F
45°F
© 2025 Daikin Applied

## Slide 54: Heat Pump Heating Emissions – Minnesota
Chart: Heat Pump COP vs Emissions
Assumptions |  | 
Natural Gas Efficiency: | 85% | 
Electric Resistance Efficiency: | 99% | 
Grid Emissions Factor: (lb/MWh) | 752 | 
Natural Gas Emissions (lbs/therm) | 12.1 | 
Elect. Heat
Nat. Gas
Heat Pump
Emissions Changeover
Increasing Efficiency
Emissions changeover varies with grid emissions factors, available from US EPA eGRID

## Slide 55: Heat Pump Heating Emissions – Minnesota
Chart: Heat Pump COP vs Cost
Assumptions |  | 
Natural Gas Efficiency: | 85% | 
Electric Resistance Efficiency: | 99% | 
Electricity Cost: ($/kWh) | $0.12 | 
Natural Gas Cost: ($/mcf) | $8.61 | 
Elect. Heat
Nat. Gas
Heat Pump
Cost Changeover
Increasing Efficiency
Cost changeover point varies with utility rates, available from US EIA and utilities

## Slide 56: Heat Pump Heating Emissions – North Carolina
Chart: Heat Pump COP vs Emissions
Assumptions |  | 
Natural Gas Efficiency: | 85% | 
Electric Resistance Efficiency: | 99% | 
Grid Emissions Factor: (lb/MWh) | 626 | 
Natural Gas Emissions (lbs/therm) | 12.1 | 
Elect. Heat
Nat. Gas
Heat Pump
Emissions Changeover
Increasing Efficiency
Emissions changeover varies with grid emissions factors, available from US EPA eGRID

## Slide 57: Heat Pump Heating Emissions – North Carolina
Chart: Heat Pump COP vs Cost
Assumptions |  | 
Natural Gas Efficiency: | 85% | 
Electric Resistance Efficiency: | 99% | 
Electricity Cost: ($/kWh) | $0.11 | 
Natural Gas Cost: ($/mcf) | $10.12 | 
Elect. Heat
Nat. Gas
Heat Pump
Cost Changeover
Increasing Efficiency
Cost changeover point varies with utility rates, available from US EIA and utilities

## Slide 58: Cold Climate Considerations
Colder climates are a challenge for HPs
    Gas density
    Motor cooling
    Capacity / efficiency
Higher LWT Operation
  Reduces HP efficiency
  Increases lift
To operate HPs in cold climates, you need to do any/all of these:
  Reduce the load
  Recover energy
  Lower the hot water temperature
  Share the lift
Temp
Capacity
Load & Lift
© 2025 Daikin Applied

## Slide 59: Why High LWT HPs Aren’t The Perfect Answer
Historically, high heating water temperature wasn’t such a big deal
  Limited impact on gas / electric resistance efficiency
  Minimizes coil and pipe sizes
  Many systems use 180°F or warmer hot water, or steam
Retrofitting these systems with heat pumps may be more difficult
  Heat pumps are lift sensitive; the warmer the hot water, the worse the efficiency and capacity
  Lower supply temperature is more efficient, but may require new pipe and heating coils
  Simply retrofitting high temperature heat pumps may not be the best overall option if environmental concerns are a design goal
Not all heat pump systems are equally difficult to retrofit
  Rooftop units may be much easier to convert from gas to heat pump than high temperature hot water systems
  The main changes on RTUs are larger electrical service and unit size
©2024 Daikin Applied
Heat Pump ≠ Boiler

## Slide 60: Retrofitting Package Rooftop HPs
New ASHP Rooftop Unit
 | Scenario 1: Std Heat Pump | Scenario 2: Inverter Heat Pump | Scenario 3: Inverter HP Dual-point Electrical
MCA | 280 amps – 300 MCM | 233 amps – 4/0 AWG | C1: 130A 1/0 AWG C2: 100A 3 AWG
MOP | 300 amps | 250 amps | C1 150A / C2 = 125A
Install Requirements | New 280A Feed (+6 wire sizes) | New 233A Feed (+3 wire sizes) | Use existing 130A Feed, New 100A Feed
Relative Electrical Install Cost | High | Medium | Low
 | Existing Unit
MCA | 130A – 1/0 AWG
MOP | 150
Existing Unit
Rooftop w/ Gas Heat
© 2025 Daikin Applied

## Slide 61: Retrofitting Package Rooftop HPs
New ASHP Rooftop Unit
 | Scenario 1: Std Heat Pump | Scenario 2: Inverter Heat Pump | Scenario 3: Inverter HP Dual-point Electrical
MCA | 280 amps – 300 MCM | 233 amps – 4/0 AWG | C1: 130A 1/0 AWG C2: 100A 3 AWG
MOP | 300 amps | 250 amps | C1 150A / C2 = 125A
Install Requirements | New 280A Feed (+6 wire sizes) | New 233A Feed (+3 wire sizes) | Use existing 130A Feed, New 100A Feed
Relative Electrical Install Cost | High | Medium | Low
 | Existing Unit
MCA | 130A – 1/0 AWG
MOP | 150
Existing Unit
Rooftop w/ Gas Heat
© 2025 Daikin Applied

## Slide 62: Retrofitting Package Rooftop HPs
New ASHP Rooftop Unit
 | Scenario 1: Std Heat Pump | Scenario 2: Inverter Heat Pump | Scenario 3: Inverter HP Dual-point Electrical
MCA | 280 amps – 300 MCM | 233 amps – 4/0 AWG | C1: 130A 1/0 AWG C2: 100A 3 AWG
MOP | 300 amps | 250 amps | C1 150A / C2 = 125A
Install Requirements | New 280A Feed (+6 wire sizes) | New 233A Feed (+3 wire sizes) | Use existing 130A Feed, New 100A Feed
Relative Electrical Install Cost | High | Medium | Low
 | Existing Unit
MCA | 130A – 1/0 AWG
MOP | 150
Existing Unit
Rooftop w/ Gas Heat
© 2025 Daikin Applied

## Slide 63: Equipment & System Efficiency
© 2025 Daikin Applied

## Slide 64: Cascade and geothermal Systems
© 2025 Daikin Applied

## Slide 65: Cascade System
Sharing the lift
Improves air-to-water heat pump low ambient performance
Share and store energy in the building for comfort or domestic hot water needs
145°F
95°F
Intermediate
Loop
Water to Water HP
Air to Water HP
© 2025 Daikin Applied

## Slide 66: Geothermal District Heating & Cooling
Avoids air source heat pump challenges
Shares heat between buildings
Could combine with data centers for heating
Potential funding:
  Utility incentives
  Tax credits
  DOE programs
© 2025 Daikin Applied

## Slide 67: Load Reduction through ventilation optimization
© 2025 Daikin Applied

## Slide 68: IAQ & Energy: A Balancing Act
IAQ
Filtration
Ventilation
EUI
Cooling
Heating
Energy
Dilution
VRP

## Slide 69: IAQ & Energy: A Balancing Act
Achieve a Better Balance
Between IAQ and Energy Performance
IAQ
Filtration
Ventilation
EUI
Cooling
Heating
Energy
IAQP

## Slide 70: IAQP: More Outside Air = More Carbon Emissions and Cost
Larger and more expensive HVAC systems
Higher energy use and carbon emissions
Increased operating costs
What if the outside air is polluted?
How buildings ensure good indoor air quality today…
…results in higher emissions & more cost
Relying on only outside air ventilation to deliver good indoor air quality is energy intensive and costly in many climates
Chart: 
| Min OA + Cleaning (IAQP) | Min OA no Cleaning (VRP) | Increased OA (VRP + 30%)
Annual Operating Cost | 1.44 | 3.09 | 4.74
More conditioned outside air to “refresh” indoor air
Better indoor air quality

## Slide 71: ASHRAE Allows for Less Outside Air with Air Scrubbing
ASHRAE Standard 62.1 includes two mechanical ventilation procedures:
 | Ventilation Rate Procedure (VRP) | Indoor Air Quality Procedure (IAQP)
Methodology | Prescriptive: Outside air based on area and occupancy without accounting for air cleaning. | Performance-based: Outside air based on IAQ design targets and source-control and removal measures.
Indoor Air Quality | Depends on quality of outside air and any unusual indoor air contaminates. | Equivalent or better than VRP, especially when outside air is polluted or unusual contaminants.
Energy Intensity | Higher in many climate zones because IAQ is achieved using only outside air. | Often lower because a portion of the outside air may be replaced with cleaned indoor air.
“The IAQP may allow for a more cost-effective solution to providing good air quality, as all design strategies may be considered and compared...” - Standard 62.1-2019 User’s Manual, Pg. 100
© 2025 Daikin Applied

## Slide 72: Building Life-Cycle Impact

## Slide 73: Building Life-Cycle Impact
Engineer
Owner
Contractor
Facility Manager
Occupant

## Slide 74: RTU Heat Pump Case Study
Eagle Street Industrial Facility
Toronto
New construction
Industrial/logistical warehouse
CaGBC Zero Carbon Building Design Standard V3
Rooftop unit heat pumps with
    R-32 refrigerant
    Optimized ventilation
    Supplemental gas heat
© 2025 Daikin Applied

## Slide 75: Where Can I Go for Information?

## Slide 76: Where Can I Go for Information?
Selected Resources
Daikin Applied: The Paths to Decarbonization
ASHRAE
  Center of Excellence for Building Decarbonization
  Building Decarb 101
US Department of Energy: Decarbonizing the U.S. Economy by 2050: A National Blueprint for the Buildings Sector
Decarbonization Guides
  Decarbonizing Building Thermal Systems: A How-To Guide for Applying Heat Pumps and Beyond
Pathways to Commercial Liftoff: Geothermal Heating and Cooling

## Slide 77: Questions & Key Takeaways
Key Takeaways
Three levers for decarbonization of HVAC systems
    Electrification, efficiency, refrigerants
  Heat pumps are work in progress
    Improving unit operating envelope
  Optimize the system
    Lower the hot water temperature
    Consider COP, emissions and cost
    Apply dual fuel / supplemental heat where it makes sense
  Share the lift, share the energy
    Cascade systems; district energy systems; heat recovery
  Reduce the load
    Optimize ventilation with IAQP

## Slide 78: Thank you for your time and attention
For more information, contact:
Jeff Seewald
jeffrey.seewald@daikinapplied.com

## Slide 79: Building Life-Cycle Impact
Plan
Design
Construct
Operate & Maintain
Renovate