## Slide 1: Introducing the Future of Refrigerants
R-32 : The Global Replacement For R-410A
DISCLAIMER: This presentation is intended only for educational purposes and does not replace independent professional judgment and/or legal advice. This presentation is copyrighted and cannot be used without the express permission of Daikin Applied Americas Inc.
©2025 Daikin Applied

## Slide 2: R-410A Replacements: R-32 and R-454B
Refrigerant | Composition | ASHRAE 34 Classification | RCL (g/m3) | GWP100 (AR4) | Glide (K) | Efficiency | Capacity | Stability | Value | LCCP
R-410A | 50% R-32 / 50% R-125 | A1 | 420 | 2088 | < 0.5 |  |  |  |  | 
R-32 | Pure 100% R-32 | A2L | 77 | 675 | 0 |  |  |  |  | 
R-454B | 68.9% R-32 / 31.1% R-1234yf | A2L | 76 | 466 | 1.5 |  |  |  |  | 
R-32 is the superior long-term choice:
All options contain R-32 in some percentage
Best in class for efficiency, ozone protection, environmental impact and value, and
Equal on safety to the other blend, R-454B
©2025 Daikin Applied

## Slide 3
©2025 Daikin Applied

## Slide 4: R-32 is a Proven Commodity Used Globally
R-32 has achieved a global installed base of over 280 million units in over 130 countries by more than 60 OEMs
Australia 2014
North America
2016
Developing
Countries
India 2013
Thailand 2014
Japan 2012
Europe 2014
PROVEN
©2025 Daikin Applied

## Slide 5: Easy to Reuse, Reclaim, and Recycle
No glide; not a blend
Reuse and clean on site, without changing the composition
Reclaim and recycle offsite in a simple cleaning process
Blends such as R-454B do not share these benefits!
EASY
UNLIKE BLENDS, R-32 IS A PURE, SINGLE-COMPONENT REFRIGERANT, MAKING IT EASY TO REUSE, RECLAIM, AND RECYCLE
©2025 Daikin Applied

## Slide 6: Easy to Service
R-32 can be changed in both liquid and gas phase
Blends like R-454B, should be charged in liquid phase as composition can change otherwise
R-32 can be topped up and recharged easily without concerns about change in composition
All of this means easier and faster service on site
EASY
UNLIKE BLENDS, R-32 IS A PURE, SINGLE-COMPONENT REFRIGERANT, MAKING IT EASY TO SERVICE
©2025 Daikin Applied

## Slide 7: Excellent Efficiency and Capacity
Figure shows COP comparisons based on simulation of a basic vapor compression cycle for an air-conditioner employing a typical forced-convection, air-to-refrigerant heat exchanger, maintaining the same heat flux in the evaporator for a fair comparison.
EFFICIENT
R-454B
R-32 has Excellent Efficiency and Capacity; Better than R-410A
©2025 Daikin Applied

## Slide 8: Flammability
Is R-32 more flammable than R-454B?
Both R-32 and R-454B are A2Ls, with similar flammability profiles
Safety & flammability limits (RCL & LFL) within about 3-4%
Both difficult to ignite, low flame velocity
Water
R-410A
Propane
R-32
R-454B
A1
A2L
A2
A3
Flammability Continuum
Refrigerant | ASHRAE 34 Classification | RCL* (g/m3) | LFL* (g/m3)
R-32 | A2L | 77 | 306
R-454B | A2L | 74 | 297
Higher number is better
*Based on updated RCL and LFL values of ASHRAE 34 -2022 Addendum a
LFL: 306
LFL: 297
LFL: 38
LFL: N/A
LFL: N/A
LFL
©2025 Daikin Applied

## Slide 9: GWP is Not the Full Measure of Emissions
  Majority of climate impact from HVAC is electrical power generation over equipment lifetime
  A lower GWP refrigerant with lower efficiency could actually create more global warming!
Direct Effect from Refrigerant
Indirect Effect from Energy Use
Life Cycle Climate Performance
(LCCP)
Source: Zhang M., et al. 2011. “Life Cycle Climate Performance Model for Residential Heat Pump Systems.” AHRTI Report 09003-01
©2025 Daikin Applied

## Slide 10: R-32: Common Misconceptions – ‘Is it as simple as GWP?’
Phasedown Schedule
Production & Import of Bulk HFCs
All sectors
CO2eq = GWP x mass
Source: US EPA
Refrigerant | Safety Class | GWP100 (AR4) | Refrigerant charge level (R-410A baseline) | 'Adjusted' GWP vs R-410A
R-410A | A1 | 2088 | 1 | 2088
R-32 | A2L | 675 | ~0.65 | ~435
R-454B | A2L | 466 | ~0.9 | ~419
Does the higher GWP of R-32 relative to R-454B mean R-32 is worse for the environment or will be phased down sooner?
-R-32’s GWP is higher than R-454B’s GWP but…
  -Charge/ton is typically lower for R-32
  -R-32 efficiency is superior
  -Produced Mass * GWP is what matters
  -Less mass of R-32 per ton of cooling is needed
©2025 Daikin Applied

## Slide 11: Efficiency and Refrigerant Charge
R-32 air-cooled scroll chiller vs. comparable R-454B scroll chiller
Actual side-by-side comparisons will vary due to non-refrigerant design factors
Tradeoff between efficiency and charge – maximizing efficiency would limit charge savings and vice-versa
19% Less
5% higher
R-32 Charge
R-32 Efficiency
R-32
R-454B
19% lower avg. charge
©2025 Daikin Applied

## Slide 12: Lifetime Emissions
*Comparison is made using the Life Cycle Climate Performance (LCCP) metric, measured in kg-CO2.eq. LCCP analysis was performed using a high efficiency HP (24+ SEER), using performance gains claimed by respective refrigerant manufacturer, for a residential sized (9000 Btu/h cooling capacity), installed in Houston, TX climate zone, with an assumed annual leakage rate of 4% and end of life refrigerant leakage of 15% with a 15 year lifetime. The heating COP and SEER were adjusted based on refrigerant characteristics and performance. The physical system size, trim charge requirements and capacity were kept consistent to ensure a like-to-like comparison.
©2025 Daikin Applied

## Slide 13: Intellectual Property & Patents
2011
Daikin offered free access to 93 patents for emerging countries
2015
Expanded free access worldwide
2019
Additional non-assertion pledge to patents filed since 2011
2021
Released 123 further patents
2022
Added 120 new patents, bringing the total to 419 to be used free of charge
R-32 TECHNOLOGY PATENT TIMELINE
No active patents on the chemical itself – used in R-410A
Technology patents have been released to allow easier adoption
R-32
Proprietary and patented
R-454B
The underlying concern is really cost, not patents, right…?
©2025 Daikin Applied

## Slide 14: R-32: Common Misconceptions - Cost
R-32 20lb Cylinder
R-454B 20lb Cylinder
Is R-32 more expensive than R-454B?
* Price source: Daikin Parts (January 2025)
**Online retailer eRefrigerants lists R-32 for $369/20lbs and R-454B for $499 per 20lb cylinder
R-410A 25lb Cylinder
$11.12 / lb
$15.70 / lb
$5.67 / lb
R-32
R-454B
R-410A
©2025 Daikin Applied

## Slide 15: R-32 Can Help Save Valuable Time, Money, and Effort
COST
Less expensive than many blends to install and maintain during servicing, saving technicians valuable time and effort on site
ACCESSIBILITY
R-32 is used globally and is the base of many blends, for several decades
©2025 Daikin Applied

## Slide 16: In Summary
Proven, easy, efficient, available, results in lower lifetime cost and emissions
R-32: An IDEAL Solution to Replace R-410A
©2025 Daikin Applied

## Slide 17: Where Can I Go for Information?
General Guidance:
https://www.daikinapplied.com/training
https://www.ahrinet.org/saferefrigerant
https://www.escogroup.org/training/lowgwprefrigerant.html
https://www.acca.org/education/a2l-refrigerants
https://www.rses.org/training/lowgwpa2l.aspx
https://www.r32reasons.com/
https://www.ashrae.org/technical-resources/bookstore/ashrae-refrigeration-resources
https://www.achrnews.com/articles/153195-understanding-a2l-refrigerants
https://www.esmagazine.com/articles/99996-a2l-refrigerants-safely-addressing-refrigerant-flammability-concerns
©2025 Daikin Applied

## Slide 18: Where Can I Go for Information?
Building Codes:
https://www.iccsafe.org/products-and-services/i-codes/a2l-refrigerants-transition/
https://www.ahrinet.org/a2l-refrigerant-building-code-map?state=OH#map
https://www.ashrae.org/technical-resources/standards-and-guidelines/read-only-versions-of-ashrae-standards
https://www.iapmo.org/media/31999/2024-umc-code-changes-randy-young.pdf
https://www.iccsafe.org/products-and-services/i-codes/a2l-refrigerants-transition/
Presentations and Podcasts
https://www.ashrae.org/news/ashraejournal/ashrae-journal-podcast-episode-37
AHRI Webcast Series
    An Introduction to A2L Refrigerants
    A2L Refrigerants Webinar Series Part 2 - Updates to Standards and Model Codes
    A2L Refrigerants Webinar Series Part 3: State and Local Codes and Available Resources
©2025 Daikin Applied

## Slide 19: Thank you for your time and attention
For more information, contact:
https://www.daikinapplied.com/decarbonization/refrigerants
©2025 Daikin Applied